## Cable Calculator
[5 empty] | Calculation Sheet | [8 empty] | Document No. | [8 empty] | Rev No.
Description | [15 empty] | Prepared By | [6 empty] | Checked By | [7 empty] | For HV
Non touching for HV cables
[31 empty] | Current - Air - 3c - 415 | [8 empty] | Touching
[16 empty] | Date | [6 empty] | Date
[31 empty] | Total DF |  |  | 0.7426
Values in RED to be altered by means of the DROP-DOWN Menus Only
| 1. Drive Details | [29 empty] | Current flow |  |  | 523.8352
| Drive Tag Number | [16 empty] | 103 |  |  |  | PMP |  |  | 1 | [5 empty] | Amp per cond |  |  | 523.8352
| Motor Nominal Mech Rating (kW) | [16 empty] | 250 |  |  |  | kW
| Motor Efficiency @ Full Load | [16 empty] | 96 |  |  |  | %
| Motor Power Factor (pf) @ Full Load | [16 empty] | 0.926 |  |  |  | pu | [8 empty] | For Current |  |  | Conductor Size |  |  |  | #N/A | mm2
| System Voltage (V) | [16 empty] | 415 |  |  |  | Volts
| 2. Motor Full Load Capacity | [29 empty] | For Voltage Drop | [6 empty] | 2.5 | mm2 |  |  | #N/A
| Full Load Current (IFL) |  |  | = | Motor Nominal Mech Rating x 1000
[5 empty] | Sqrt(3) x System Voltage x Efficiency x Powerfactor | [32 empty] | 1
389
| From Motor Data Tables |  |  | = | 389 |  |  | Amps | [8 empty] | = | 389 |  |  |  | Amps (at 50Hz)
3. Motor Cable Selection
| Selections as per AS3008.1.1:2009 | [30 empty] | Cable Ladder - 3 Tier
| Cables to be used shall have a temperature rating of 90°C | [30 empty] | 45 | [9 empty] | Cable Ladder - 3 Tier | Temp | 45 |  | Cable spacing |  | Touching
| Installation Type | [10 empty] | Cable Ladder - 3 Tier | [19 empty] | Touching | [9 empty] | Conduit - In Ground | Temp | 30 |  | Cable spacing |  | 0.3
| Cable Location | [10 empty] | Air
| Cable Type | [10 empty] | Standard
| Ambient Temperature | [10 empty] | 45 |  |  |  | oC
| Derating Factor (DF) - Ambient | [10 empty] | 0.94 | [6 empty] | AS3008, |  |  | Table 27(1)
| Number of Circuits per Ladder / Conduit | [10 empty] | 3 | [18 empty] | For LV
| Cable Spacing | [10 empty] | Touching
| Derating Factor (DF) - Cable Spacing | [10 empty] | 0.79 | [6 empty] | AS3008, |  |  | Table 24, Item 15 | [12 empty] | Std | [9 empty] | 1
| Number of Layers on Ladder | [10 empty] | 2 | [22 empty] | Current - Air - 3c - XLPE - Std | [9 empty] | 1.5
| Derating Factor (DF) - # of Layers on Ladder | [10 empty] | 0.936 | [20 empty] | Total DF |  | 0.7426 | [9 empty] | 2.5
| Depth of Cable Laying | [10 empty] | 0.5 |  |  |  | metres | [16 empty] | Current flow |  | 523.8352 | [9 empty] | 4
| Derating Factor (DF) - Depth of Cable Laying | [10 empty] | N/A | [6 empty] | AS3008, Table 28 | [13 empty] | Amp per cond |  | 523.8352 | [9 empty] | 6
| Cable Voltage Rating | [10 empty] | 0.6/1.0 |  |  |  | kV | [28 empty] | 10
| Single / Multi Core Configuration | [10 empty] | 3c | [6 empty] | Arranged as: |  |  |  |  | 1 x 3c |  |  |  |  | For Current |  |  |  | Conductor Size |  |  | 300 | mm2 | [7 empty] | 16
| Soil Characteristics (For u/g use only): | [10 empty] | 1.2 General except very dry light soils | [32 empty] | 25
| (Select best description/value) | [43 empty] | 35
| Soil Thermal Resistivity | [10 empty] | 1.2 |  |  |  | °C.m/W | [12 empty] | For Voltage Drop | [6 empty] | 185 | mm2 |  |  |  | 300 |  |  |  | 50
| Soil Derating Factor | [10 empty] | N/A | [6 empty] | AS3008 Table 29 + interpolations | [25 empty] | 70
| Conductor Insulation | [10 empty] | XLPE | [32 empty] | 95
| Selected Cable Size | [10 empty] | 300 |  |  |  | mm2 | [19 empty] | 1 | [8 empty] | 120
| Conductor Size Factor (For U/Gnd Use Only ) | [10 empty] | N/A | [32 empty] | 150
| Conductor (NOTE: Only Cu is used for HV calcs) | [10 empty] | Cu | [32 empty] | 185
| Nominal Current Rating (per cable) | [10 empty] | 594 |  |  |  | Amps |  |  | AS3008, |  |  | Table 14, Column 2 | [22 empty] | 240
| Number of Cores in Parallel per Phase | [10 empty] | 1 | [32 empty] | 300
400
| Harmonic Current Considerations: | [28 empty] | Selection of cable type | [6 empty] | VSD | [7 empty] | 500
[12 empty] | 20 |  |  |  | % |  |  | <== Not used | [25 empty] | 630
| Neutral Conductor 50Hz Current | [10 empty] | 0 |  |  |  | Amps |  |  | <== Not used | [17 empty] | XLPE
| Are Harmonics Present | [10 empty] | No | [6 empty] | Harmonics arise from
| Harmonics as % of Phase Current | [10 empty] | 46 |  |  |  | % |  |  | VSD Drives, etc
| Phase Conductor Reduction Factor | [10 empty] | 1 | [6 empty] | By % of Harmonic Current
| Neutral Harmonic Current Reduction Factor | [10 empty] | 1
4. Cable Phase and Neutral Conductor Current Rating & Size Checks
| Worst Case: 3 cables bunched in 1 layer (Under Sub) or 5 cables bunched, in 2 layers on ladder (Plant area) or 6 cables in conduit under ground | [33 empty] | Conductor Size |  |  | 300 |  |  | 300
[15 empty] | Under Sub | [6 empty] | In Field |  |  |  |  | Conduit
Actual Conductors Currents
| Phase Current Including Harmonic Component | [9 empty] | = | 389 |  |  |  | Amps
| Neutral Current Including Harmonic Component | [9 empty] | = | No Neutral
| Minimum Cable Rating must be | [9 empty] | = | 389 |  |  |  | Amps
|  |  | Cable Full Load Rating | = | # of Cores/Ph x Nominal Current Rating x Ambient DF x Spacing DF x Layers DF * Harmonic RF
|  |  |  | = | [7 empty] | 412.8737 |  |  |  | Amps
|  |  | Cable Spare Capacity | = | Cable Full Load Rating (for FLC)
|  |  |  | = | [7 empty] | 23.8737 |  |  |  | Amps |  |  | = | 5.782% |  |  | Spare Capacity
| Conclusion |  |  | = | Cable Selection is Satisfactory for Current Rating
Use 1 off 1 x 3c 300mm2 Cu XLPE 0.6/1.0kV
Indicative Max Run
| 4. Volt Drop Capacity | [21 empty] | 123.572 |  |  |  | metres
| Motor Cable Route Length | [10 empty] | 150 |  |  |  | metres
| Motor Starting Power Factor (pf) | [10 empty] | 0.2 | [6 empty] | AS3851
| Cable Volt Drop | [10 empty] | 0.259 |  |  |  | mV/A.m |  |  | AS3008, |  |  | Table 42 & 90°C
| Cable Resistance (Rc) | [10 empty] | 0.129 |  |  |  | W/km |  |  | AS3008, |  |  | Table 35
| Cable Reactance (Xc) | [10 empty] | 0.0704 |  |  |  | W/km |  |  | AS3008, |  |  | Table 30
| Type of Starting (ie DOL, VSD, SST, LRS) | [10 empty] | VSD
| Motor Starting Current (x FLC) | [10 empty] | 2 |  |  |  | pu
| Running Volt Drop |  | = | Motor FLC x Motor Cable Route Length x Cable Volt Drop (mV/A.m)
No of Conductors/Phase x 1000
|  | by mV/A.m | = | 15.1127 |  |  | Volts | [10 empty] | by Cable Impedance | = | 14.8525 |  |  | Volts
| % Volt Drop (Running) |  | = | Running Volt Drop x 100 | [20 empty] | Max VD = | 3 |  | %
System Voltage
|  | by mV/A.m | = | 3.6416 |  |  | % | [10 empty] | by Cable Impedance | = | 3.5789 |  |  | %
| Starting Volt Drop |  | = | Motor Starting Current x Motor Cable Route Length x Cable Volt Drop (mV/A.m)
No of Conductors/Phase x 1000
|  | by mV/A.m | = | 30.2253 |  |  | Volts | [10 empty] | by Cable Impedance | = | 29.705 |  |  | Volts
| % Volt Drop (Starting) |  | = | Starting Volt Drop x 100 | [20 empty] | Max VD = | 15 |  | %
System Voltage
|  | by mV/A.m | = | 7.2832 |  |  | % | [10 empty] | by Cable Impedance | = | 7.1578 |  |  | %
| Conclusion |  | = | Please revise cable selection
5. Cable Thermal Loading
| Cable Thermal Loading |  | = |  |  |  |  | Full Load Current |  |  |  |  | 2
Cable De-rated Capacity
|  |  | = | 88.7697 |  |  | %
6. Cable Fault (Short Circuit) Rating Check
| Design Fault Level | [10 empty] | 70 |  |  |  | kA
| Design Fault Duration | [10 empty] | 0.2 |  |  |  | sec
| Selected Conductor Size | [10 empty] | 300 |  |  |  | mm2
| Conductor Insulation | [10 empty] | XLPE
| Conductor Material | [10 empty] | Cu
| No Conductors per Phase | [10 empty] | 1
| Initial Conductor Temperature | [10 empty] | 90 |  |  |  | °C
| Final Conductor Temperature | [10 empty] | 250 |  |  |  | °C |  |  | AS3008, |  |  | Table 52
| Constant K | [10 empty] | 143 | [6 empty] | AS3008, |  |  | Table 51
| Minimum Total Conductor Size |  | = | [6 empty] | ( Fault Current) | 2 | x | Fault Duration
[12 empty] | ( constant K ) | 2
|  |  | = | [8 empty] | 218.9157 |  |  |  | mm2
| Minimum Conductor Size |  | = |  |  | Min Total Conductor Size
No of Conductors / Phase
|  |  | = | [8 empty] | 218.9157 |  |  |  | mm2
| Conclusion |  | = | Cable selection is satisfactory for fault level
| 7. Earth Conductor Checks | [7 empty] | (As per AS2067 the 25% rule does not apply to earths between the LV secondary of distribution transformers and substation earth)
| Is an Earth Conductor required | [15 empty] | Yes
| Does Circuit Protection Include Earth Leakage Protection | [15 empty] | No
| Phase/Active Cable Conductor Size | [15 empty] | 300 |  |  |  | mm2
| Number of Active Cores in Parallel per Phase | [15 empty] | 1
| Summation of Active Conductors Cross Sectional Area | [15 empty] | 300 |  |  |  | mm2
Fix for HV cables
| Cable Internal Earth Conductor Size | [15 empty] | 120
[17 empty] | 95 |  |  |  | <==== |  |  | Ignored
| No of Earth Cores internal to Multi-core Cables | [15 empty] | 1
[17 empty] | 4 | [6 empty] | Ignored
| Is there a further 'Running Earth' that provides a Return Path | [15 empty] | No
[17 empty] | 120 |  |  |  | <==== |  |  | Ignore
| Summation of Earth Conductors Cross Sectional Area | [15 empty] | 120 |  |  |  | mm2
Check Sum earth conductor area > 25% sum of active conductor areas
| Earth Cable Size as % of Sum of Active Conductor Size | [15 empty] | 40 |  |  |  | %
7.1 Minimum Cross Sectional Area of Earth Conductor
| Design 1Ph to Earth Fault Level | [15 empty] | 25 |  |  |  | kA
| Design Fault Duration | [15 empty] | 1 |  |  |  | sec
| Selected Conductor Size | [15 empty] | 120 |  |  |  | mm2
| Conductor Insulation | [15 empty] | PVC-V90
| Conductor Material | [15 empty] | Cu
| No Conductors in parallel | [15 empty] | 4
| Initial Conductor Temperature | [15 empty] | 40 |  |  |  | °C
| Final Conductor Temperature | [15 empty] | 160 |  |  |  | °C |  |  | AS3008, |  |  | Table 52
| Constant K | [15 empty] | 136 | [6 empty] | AS3008, |  |  | Table 51
| Minimum Total Conductor Size |  | = | [6 empty] | ( Fault Current) | 2 | x | Fault Duration | [10 empty] | AS3008, Eq 5.3(1)
( constant K )2
|  |  | = | [8 empty] | 183.8235 |  |  |  | mm2
| Minimum Conductor Size for each Earth |  | = |  |  | Min Total Conductor Size
No of Conductors
discounts any 'Running Earth' smaller
|  |  | = | [8 empty] | 45.9559 |  |  |  | mm2 |  |  |  | than the primary earth cores laid
with the phases conductors
7.3 Earth Fault Loop Maximum Circuit Length Check
| Conductor (NOTE: Only Cu is used for earth conductor) | [15 empty] | Cu
| Nominal Phase Voltage (Uo) | [15 empty] | 239.6004 |  |  |  | V
| Resistivity at Normal Temperature (p) | [15 empty] | 0.0225 |  |  |  | Wmm2/m
| Protective device | [13 empty] | Circuit Breaker
| Circuit Breaker Type | [15 empty] | MCCB
| Circuit Breaker Rating | [6 empty] | if motor 2 x FLC | [8 empty] | 200 |  |  |  | A
| Miniature Circuit Breaker Curve | [6 empty] | if feeder = FLC | [8 empty] | Type C |  |  |  | Not MCB, Use curve C
| Mean Tripping Current Factor | [15 empty] | 7.5 |  |  |  | x rated current |  |  |  |  | AS3000 B.4
| Mean Tripping Current (Ia) | [15 empty] | 1500 |  |  |  | A
| Active Conductor Total Cross Sectional Area (Sph) | [15 empty] | 300 |  |  |  | mm2
| Earth Conductor Total Cross Sectional Area (Spe) | [15 empty] | 120 |  |  |  | mm2
| Cable route length | [15 empty] | 150 |  |  |  | m
| Maximum Length |  | = |  |  | 0.80*Uo*Sph*Spe | [14 empty] | AS/NZS 3000 |  |  |  |  | B7
Ia*p*(Sph+Spe)
|  |  | = | [8 empty] | 486.8071 |  |  |  | m
| Conclusions |  | = | Earth Conductor Sizing is Satisfactory
Please revise earth cable selection - Earth conductor size cannot handle
Earth cable earth fault loop impedance is satisfactory for route length
Note on AB11: Select - TNF for Transformer, - MCC for Motor Control Centre, - EDB for Distribution board, - or other codes to suit or other drive types
Note on X12: Change Value depending if the Equipment is: - DB Feeder (Amps) - MCC Feeder (Amps) - Transformer (kVA), or - Drive Motor (kW)
Note on X13: Value changes to 100% if equipment is a Transformer, DB or MCC Feeder
Note on X14: Value changes to 100% if equipment is a Transformer, DB or MCC Feeder