## Cable Lookup
|  | Copper LV Cable Current Rating | [19 empty] | Lookup Data
Cable Size [mm2] | Lookup Row Number | Current - Air - 1c - XLPE - Std | Current - Air - 1c - XLPE - Flex | Current - Air - 1c - PVC-V90 - Std | Current - Air - 1c - PVC-V90 - Flex | Current - Ground - 1c - XLPE - Std | Current - Ground - 1c - PVC-V90 ` | Current - Enclosure - 1c - XLPE - Std | Current - Enclosure - 1c - XLPE - Flex | Current - Enclosure - 1c - PVC-V90 - Std | Current - Enclosure - 1c - PVC-V90 - Flex | Current - Air - 3c - XLPE - Std | Current - Air - 3c - XLPE - Flex | Current - Air - 3c - PVC-V90 - Std | Current - Air - 3c - PVC-V90 - Flex | Current - Ground - 3c - XLPE - Std | Current - Ground - 3c - PVC-V90 - Std | Current - Enclosure - 3c - XLPE - Std | Current - Enclosure - 3c - XLPE - Flex | Current - Enclosure - 3c - PVC-V90 - Std | Current - Enclosure - 3c - PVC-V90 - Flex
1 | 2 | 16 | 17 | 14 | 14 | 18 | 16 | 18 | 19 | 16 | 16 | 16 | 16 | 13 | 13 | 16 | 14 | 16 | 17 | 14 | 15 | 16 |  |  |  |  | MATCH(MIN(IF(A3:A22>A30,A3:A22)) | INDEX($A$3:$V$22,MATCH(MIN(IF(A3:A22>A30,A3:A22)),$A$3:$A$22,0),MATCH($A$29,$A$2:$V$2,0))
1.5 | 3 | 21 | 22 | 17 | 18 | 22 | 20 | 22 | 23 | 20 | 20 | 20 | 20 | 16 | 17 | 20 | 18 | 20 | 21 | 18 | 18 | 20
2.5 | 4 | 30 | 29 | 25 | 24 | 31 | 27 | 31 | 30 | 27 | 26 | 28 | 27 | 23 | 22 | 29 | 25 | 29 | 28 | 25 | 24 | 28
4 | 5 | 40 | 38 | 33 | 32 | 40 | 36 | 40 | 38 | 36 | 35 | 38 | 36 | 31 | 30 | 37 | 33 | 37 | 36 | 33 | 32 | 38
6 | 6 | 50 | 49 | 42 | 41 | 50 | 45 | 50 | 49 | 45 | 43 | 48 | 46 | 40 | 38 | 46 | 42 | 46 | 45 | 42 | 40 | 48
10 | 7 | 69 | 69 | 58 | 57 | 67 | 59 | 67 | 66 | 59 | 58 | 66 | 66 | 54 | 54 | 63 | 55 | 63 | 62 | 55 | 54 | 66
16 | 8 | 92 | 91 | 77 | 75 | 117 | 104 | 86 | 85 | 78 | 76 | 88 | 87 | 72 | 71 | 110 | 96 | 81 | 79 | 73 | 71 | 88
25 | 9 | 125 | 121 | 103 | 100 | 151 | 134 | 113 | 109 | 100 | 97 | 119 | 116 | 97 | 94 | 143 | 125 | 107 | 103 | 94 | 91 | 119
35 | 10 | 154 | 151 | 127 | 125 | 180 | 160 | 137 | 134 | 122 | 119 | 147 | 144 | 120 | 117 | 172 | 150 | 130 | 127 | 114 | 112 | 147
50 | 11 | 188 | 191 | 156 | 157 | 214 | 190 | 163 | 163 | 144 | 145 | 180 | 182 | 146 | 148 | 204 | 179 | 155 | 155 | 136 | 137 | 180
70 | 12 | 240 | 241 | 197 | 198 | 262 | 233 | 203 | 203 | 180 | 180 | 229 | 230 | 185 | 185 | 251 | 219 | 193 | 193 | 170 | 169 | 229
95 | 13 | 298 | 290 | 246 | 239 | 313 | 279 | 244 | 237 | 217 | 210 | 283 | 275 | 228 | 222 | 302 | 263 | 233 | 226 | 208 | 201 | 283
120 | 14 | 349 | 346 | 287 | 284 | 356 | 317 | 284 | 279 | 252 | 247 | 330 | 327 | 265 | 262 | 344 | 300 | 270 | 266 | 237 | 232 | 330
150 | 15 | 403 | 400 | 330 | 328 | 400 | 356 | 320 | 316 | 283 | 279 | 377 | 375 | 303 | 301 | 385 | 336 | 304 | 300 | 266 | 265 | 377
185 | 16 | 468 | 459 | 383 | 376 | 452 | 402 | 363 | 357 | 325 | 316 | 436 | 428 | 348 | 342 | 435 | 379 | 348 | 339 | 304 | 296 | 436
240 | 17 | 560 | 553 | 457 | 451 | 523 | 465 | 426 | 416 | 377 | 376 | 517 | 511 | 412 | 407 | 504 | 438 | 411 | 402 | 359 | 351 | 517
300 | 18 | 648 | 637 | 529 | 519 | 589 | 524 | 491 | 479 | 434 | 423 | 594 | 584 | 472 | 464 | 567 | 493 | 463 | 452 | 404 | 394 | 594
400 | 19 | 756 | 764 | 615 | 621 | 668 | 593 | 557 | 554 | 492 | 504 | 685 | 692 | 544 | 549 | 640 | 557 | 524 | 537 | 468 | 467 | 685
500 | 20 | 874 | 884 | 710 | 717 | 752 | 668 | 648 | 642 | 571 | 566 | 779 | 794 | 616 | 627 | 714 | 620 | 601 | 602 | 522 | 523 | 779
630 | 21 | 1010 | 1030 | 817 | 833 | 843 | 748 | 727 | 729 | 639 | 641 | [10 empty] | 0
AS3008 |  | Table 8, Column 5 | Table 8, Column 6 | Table 7, Column 5 | Table 7, Column 6 | Table 8, Column 22 | Table 7, Column 22 | Table 8, Column 24 | Table 8, Column 25 | Table 7, Column 24 | Table 7, Column 25 | Table 14, Column 2 | Table 14, Column 3 | Table 13, Column 2 | Table 13, Column 3 | Table 14, Column 23 | Table 13, Column 23 | Table 14, Column 25 | Table 14, Column 26 | Table 13, Column 25 | Table 13, Column 26
Current - Air - 3c - XLPE - Std
523.8352
300
|  | MV Cable Current Rating from Olex HV Cable Catalogue = NOTE 3C is not SWA in this TABLE NOTE: ENCLOSURE IS ASSUMED UNDERGROUND, GROUND IS ASSUMED DIRECT UNDERGROUND | [29 empty] | Lookup Data
Cable Size [mm2] | Lookup Row Number | Current - Air - 1c - 3300 | Current - Air - 1c - 6600 | Current - Air - 1c - 11000 | Current - Air - 1c - 22000 | Current - Air - 1c - 33000 | Current - Ground - 1c - 3300 | Current - Ground - 1c - 6600 | Current - Ground - 1c - 11000 | Current - Ground - 1c - 22000 | Current - Ground - 1c - 33000 | Current - Enclosure - 1c - 3300 | Current - Enclosure - 1c - 6600 | Current - Enclosure - 1c - 11000 | Current - Enclosure - 1c - 22000 | Current - Enclosure - 1c - 33000 | Current - Air - 3c - 3300 | Current - Air - 3c - 6600 | Current - Air - 3c - 11000 | Current - Air - 3c - 22000 | Current - Air - 3c - 33000 | Current - Ground - 3c - 3300 | Current - Ground - 3c - 6600 | Current - Ground - 3c - 11000 | Current - Ground - 3c - 22000 | Current - Ground - 3c - 33000 | Current - Enclosure - 3c - 3300 | Current - Enclosure - 3c - 6600 | Current - Enclosure - 3c - 11000 | Current - Enclosure - 3c - 22000 | Current - Enclosure - 3c - 33000
16 | 2 | 110 | 110 | 112 | 0 | 0 | 113 | 113 | 113 | 0 | 0 | 91 | 91 | 91 | 0 | 0 | 108 | 108 | 110 | 0 | 0 | 113 | 113 | 113 | 0 | 0 | 86 | 86 | 89 | 0 | 0 | #N/A
25 | 3 | 143 | 143 | 145 | 0 | 0 | 145 | 145 | 145 | 0 | 0 | 116 | 116 | 117 | 0 | 0 | 141 | 141 | 143 | 0 | 0 | 145 | 145 | 145 | 0 | 0 | 111 | 111 | 114 | 0 | 0 | #N/A
35 | 4 | 176 | 176 | 178 | 182 | 0 | 174 | 174 | 174 | 174 | 0 | 139 | 139 | 140 | 144 | 0 | 171 | 171 | 173 | 178 | 0 | 173 | 173 | 173 | 173 | 0 | 134 | 134 | 136 | 140 | 0 | #N/A
50 | 5 | 210 | 210 | 213 | 217 | 221 | 204 | 204 | 204 | 205 | 205 | 164 | 164 | 167 | 172 | 174 | 205 | 205 | 208 | 213 | 217 | 204 | 204 | 204 | 204 | 205 | 159 | 159 | 162 | 168 | 170 | #N/A
70 | 6 | 264 | 264 | 266 | 269 | 273 | 249 | 249 | 249 | 249 | 249 | 202 | 202 | 204 | 209 | 216 | 256 | 256 | 259 | 265 | 269 | 249 | 249 | 249 | 250 | 250 | 195 | 195 | 199 | 205 | 213 | #N/A
95 | 7 | 321 | 321 | 321 | 327 | 332 | 296 | 296 | 296 | 297 | 297 | 241 | 241 | 242 | 249 | 258 | 313 | 313 | 317 | 323 | 328 | 298 | 298 | 299 | 299 | 299 | 237 | 237 | 242 | 246 | 255 | #N/A
120 | 8 | 367 | 367 | 370 | 377 | 381 | 335 | 335 | 336 | 336 | 336 | 273 | 273 | 279 | 282 | 292 | 363 | 363 | 367 | 373 | 377 | 339 | 339 | 340 | 340 | 341 | 270 | 270 | 276 | 280 | 290 | #N/A
150 | 9 | 415 | 415 | 419 | 425 | 430 | 373 | 373 | 374 | 374 | 375 | 309 | 309 | 311 | 314 | 325 | 411 | 411 | 415 | 422 | 427 | 379 | 379 | 380 | 381 | 381 | 307 | 307 | 310 | 321 | 324 | #N/A
185 | 10 | 474 | 474 | 478 | 485 | 490 | 419 | 419 | 420 | 421 | 421 | 348 | 348 | 350 | 362 | 366 | 472 | 472 | 476 | 483 | 488 | 429 | 429 | 429 | 430 | 431 | 348 | 348 | 350 | 363 | 366 | #N/A
240 | 11 | 558 | 558 | 561 | 568 | 574 | 481 | 481 | 482 | 483 | 485 | 400 | 400 | 402 | 417 | 420 | 559 | 559 | 563 | 570 | 575 | 496 | 496 | 497 | 498 | 499 | 404 | 404 | 416 | 421 | 424 | #N/A
300 | 12 | 636 | 636 | 639 | 647 | 653 | 537 | 537 | 538 | 541 | 542 | 460 | 460 | 462 | 466 | 469 | 642 | 642 | 645 | 652 | 558 | 559 | 559 | 560 | 562 | 563 | 468 | 468 | 470 | 474 | 478 | #N/A
400 | 13 | 732 | 732 | 735 | 743 | 750 | 604 | 604 | 605 | 607 | 610 | 518 | 518 | 519 | 523 | 547 | 744 | 744 | 746 | 754 | 759 | 634 | 634 | 635 | 638 | 640 | 532 | 532 | 534 | 539 | 562 | #N/A
500 | 14 | 0 | 0 | 837 | 847 | 854 | 0 | 0 | 674 | 679 | 682 | 0 | 0 | 580 | 585 | 611 | 0 | 0 | 850 | 859 | 864 | 0 | 0 | 710 | 714 | 718 | 0 | 0 | 597 | 624 | 630 | #N/A
630 | 15 | 0 | 0 | 948 | 959 | 969 | 0 | 0 | 746 | 752 | 759 | 0 | 0 | 642 | 673 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
800 | 16 | 0 | 0 | 1082 | 1093 | 1103 | 0 | 0 | 822 | 829 | 838 | 0 | 0 | 734 | 741 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
1000 | 17 | 0 | 0 | 0 | 1295 | 1300 | 0 | 0 | 0 | 961 | 966 | 0 | 0 | 0 | 856 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
1200 | 18 | 0 | 0 | 0 | 1420 | 1426 | 0 | 0 | 0 | 1036 | 1043 | 0 | 0 | 0 | 921 | 948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A
OLEX | 2011 | Use Cat Page 6 | Cat Page 6 | Cat Page 8 | Cat Page 10 | Cat Page 12 | Use Cat Page 6 | Cat Page 6 | Cat Page 8 | Cat Page 10 | Cat Page 12 | Use Cat Page 6 | Cat Page 6 | Cat Page 8 | Cat Page 10 | Cat Page 12 | Use Cat Page1 6 | Cat Page16 | Cat Page 18 | Cat Page 20 | Cat Page 22 | Use Cat Page1 6 | Cat Page16 | Cat Page 18 | Cat Page 20 | Cat Page 22 | Use Cat Page1 6 | Cat Page16 | Cat Page 18 | Cat Page 20 | Cat Page 22
Current - Air - 3c - 415
523.8352
#N/A