## Database
415V MOTORS
| kW | Efficiency | Power Factor | Eff | pf |  |  |  |  | Eff @ 75% | pf @ 75% |  | Max cable size termiantion for motors |  |  | Code | Description
| 0.06 | 0.545 | 0.55 | [6 empty] | 0.545 | 0.55 |  | Frame size | kW rating | Max. cable size (mm2) | AA | Analyser Online | 1 PAIR | VSD | Yes | PC | 415
| 0.09 | 0.545 | 0.55 | [6 empty] | 0.545 | 0.55 |  | D80 | 0.75 | 10 | AG | Agitator / Stirrer | 2 PAIR | DOL | No | Laptop | 6600
| 0.12 | 0.6 | 0.63 | 0.6 | 0.63 |  |  |  |  | 0.558 | 0.536 |  | D90 | 1.1 | 10 | BB | Bag Breaker | 4 PAIR | FEEDER |  |  | 240
| 0.18 | 0.635 | 0.7 | 0.635 | 0.7 | 63.5 | 70 |  |  | 0.63 | 0.61 |  | D90 | 1.5 | 10 | BR | Brakes | 6 PAIR | DOL Reversing |  |  | 24
| 0.25 | 0.7 | 0.7 | 0.745 | 0.695 | 74.5 | 69.5 |  |  | 0.73 | 0.605 |  | D100 | 2.2 | 10 | BL | Blower | 8 PAIR | DOL Dual
| 0.37 | 0.745 | 0.695 | 0.715 | 0.74 | 71.5 | 74 |  |  | 0.705 | 0.65 |  | D100 | 3 | 10 | CN | Crane / Hoist | 10 PAIR | VSD Dual
| 0.55 | 0.715 | 0.74 | 0.845 | 0.745 | 84.5 | 74.5 |  |  | 0.82 | 0.65 |  | D112 | 4 | 10 | CO | Chiller | 12 PAIR
| 0.7 | 0.75 | 0.74 | 0.86 | 0.805 | 86 | 80.5 |  |  | 0.865 | 0.735 |  | D132 | 5.5 | 50 | CP | Compressor | 16 PAIR
| 0.75 | 0.845 | 0.745 | 0.87 | 0.76 | 87 | 76 |  |  | 0.86 | 0.67 |  | D132 | 7.5 | 50 | CR | Crusher | 20 PAIR
| 1.1 | 0.86 | 0.805 | 0.885 | 0.81 | 88.5 | 81 |  |  | 0.88 | 0.73 |  | D160 | 11 | 50 | CV | Conveyor | 24 PAIR
| 1.5 | 0.87 | 0.76 | 0.895 | 0.78 | 89.5 | 78 |  |  | 0.875 | 0.69 |  | D160 | 15 | 50 | DC | Dust Collector | 36 PAIR
| 2.2 | 0.885 | 0.81 | 0.9 | 0.82 | 90 | 82 |  |  | 0.895 | 0.76 |  | D180 | 18.5 | 50 | DR | Drier
| 3 | 0.895 | 0.78 | 0.91 | 0.855 | 91 | 85.5 |  |  | 0.905 | 0.81 |  | D180 | 22 | 50 | FC | Flotation Cell
| 4 | 0.9 | 0.82 | 0.917 | 0.85 | 91.7 | 85 |  |  | 0.92 | 0.805 |  | D200 | 30 | 95 | FD | Feeder
| 5.5 | 0.91 | 0.855 | 0.929 | 0.86 | 92.9 | 86 |  |  | 0.925 | 0.825 |  | D225 | 37 | 95 | FN | Fan / Flower
| 7.5 | 0.917 | 0.85 | 0.93 | 0.86 | 93 | 86 |  |  | 0.93 | 0.83 |  | D225 | 45 | 95 | FT | Filter
| 11 | 0.929 | 0.86 | 0.94 | 0.83 | 94 | 83 |  |  | 0.94 | 0.76 |  | D250 | 55 | 185 | GA | Gate (Isolation)
| 15 | 0.93 | 0.86 | 0.945 | 0.83 | 94.5 | 83 |  |  | 0.94 | 0.765 |  | D250 | 75 | 185 | HE | Heater / Oven
| 18.5 | 0.94 | 0.83 | 0.945 | 0.86 | 94.5 | 86 |  |  | 0.945 | 0.845 |  | D280 | 90 | 185 | HP | Hydraulic Power Pack
| 22 | 0.945 | 0.83 | 0.954 | 0.85 | 95.4 | 85 |  |  | 0.95 | 0.82 |  | D280 | 110 | 185 | HPP | Hydraulic Power Pack
| 30 | 0.945 | 0.86 | 0.954 | 0.855 | 95.4 | 85.5 |  |  | 0.95 | 0.82 |  | D315 | 132 | 185 | HX | Heat Exchanger
| 37 | 0.954 | 0.85 | 0.958 | 0.86 | 95.8 | 86 |  |  | 0.95 | 0.835 |  | D315 | 150 | 185 | LS | Lubrication System
| 45 | 0.954 | 0.855 | 0.957 | 0.86 | 95.7 | 86 |  |  | 0.95 | 0.845 |  | D315 | 185 | 185 | MD | Metal Detector
| 55 | 0.958 | 0.86 | 0.962 | 0.865 | 96.2 | 86.5 |  |  | 0.955 | 0.836 |  |  |  |  | MG | Magnet
| 75 | 0.957 | 0.86 | 0.964 | 0.875 | 96.4 | 87.5 |  |  | 0.963 | 0.84 |  |  |  |  | ML | Mill
| 90 | 0.962 | 0.865 | 0.967 | 0.88 | 96.7 | 88 |  |  | 0.959 | 0.845 |  |  |  |  | MS | Magnetic Separator
| 110 | 0.964 | 0.875 | 0.969 | 0.88 | 96.9 | 88 |  |  | 0.96 | 0.845 |  |  |  |  | PP | Pump
| 132 | 0.967 | 0.88 | 0.97 | 0.885 | 97 | 88.5 |  |  | 0.96 | 0.85 |  |  |  |  | RB | Rock Breaker
| 150 | 0.969 | 0.88 | 0.961 | 0.87 | 96.1 | 87 |  |  | 0.956 | 0.839 |  |  |  |  | SA | Sampler
| 160 | 0.96 | 0.88 | 0.961 | 0.87 | 96.1 | 87 |  |  | 0.957 | 0.841 |  |  |  |  | SK | Stack / Flue
| 185 | 0.97 | 0.885 | 0.962 | 0.875 | 96.2 | 87.5 |  |  | 0.958 | 0.84 |  |  |  |  | SN | Screen
| 200 | 0.965 | 0.87 | [12 empty] | ST | Shaking Table
| 220 | 0.961 | 0.87 | [12 empty] | TH | Thickener
| 250 | 0.961 | 0.87 | [12 empty] | WN | Winch
| 260 | 0.961 | 0.87 | [12 empty] | WT | Weightometer / Scale
| 265 | 0.961 | 0.87 | [12 empty] | XA
| 300 | 0.961 | 0.87 | [12 empty] | XM
| 315 | 0.962 | 0.875
| 335 | 0.962 | 0.875
| 355 | 0.962 | 0.875
| 375 | 0.96 | 0.865
| 400 | 0.96 | 0.865
| 450 | 0.965 | 0.85
| 465 | 0.965 | 0.85
| 500 | 0.965 | 0.85
| 510 | 0.965 | 0.85 |  |  |  |  | TYPICAL LOAD FACTORS |  |  | Sum Rating | Contingency
| 700 | 0.965 | 0.85 | [7 empty] | 1 | 50% | Unknown (Estimate Only)
| 710 | 0.967 | 0.83 |  |  |  |  | DRIVE/LOAD | LOAD FACTOR |  | 2 | 40% | Factored from Client (PFS Data)
| 800 | 0.969 | 0.819 | [7 empty] | 3 | 30% | Pre Award Tender Data
| 1500 | 0.967 | 0.823 |  |  |  |  | SAG MILL | 0.85 |  | 4 | 22% | Prelim Post Award Data
| 6000 | 0.96 | 0.82 | [7 empty] | 5 | 20% | Final Certified Vendor Data (AS BUILT)
[8 empty] | BALL MILL | 0.85
[8 empty] | ROD MILL | 0.85
| VSD |  | 0.9 |  |  |  |  | VERTIMILL | 0.85
[8 empty] | JAW CRUSHERS | 0.2
| NOTES :- | 1. Information derived from TECO MAX E3 Range Squirrel Cage Motors | [5 empty] | CONE CRUSHERS | 0.75
|  | 2. Both Efficiency and Power Factor calculated at 75% motor load. | [5 empty] | CONVEYORS | 0.9
|  | 3. Motor Speed is 1400rpm. | [5 empty] | FEEDERS | 0.85
[8 empty] | CENTRIFUGAL PUMPS | 0.85
|  | LOAD FACTOR | DIVERSITY |  |  |  |  | POSITIVE DISP PUMPS | 0.85
AA | ANALYSER ONLINE | 0.7 | 0.95 |  |  |  |  | SUMP PUMPS | 0.4
AG | AGITATOR / STIRRER | 0.85 | 0.95 |  |  |  |  | VACUUM PUMPS | 0.85
BB | BAG BREAKER | 0.9 | 0.1 |  |  |  |  | COMPRESSORS | 0.9
BR | BRAKES | 0.75 | 0.95 |  |  |  |  | SCREENS | 0.9
BL | BLOWER | 0.8 | 0.95 |  |  |  |  | THICKENER RAKE DRIVE | 0.9
CN | CRANE / HOIST | 0.5 | 0.1 |  |  |  |  | AGITATORS | 0.85
CO | CHILLER | 0.85 | 0.95 |  |  |  |  | E/WINNING RECTIFIERS | 0.9
CP | COMPRESSOR | 0.9 | 0.95 |  |  |  |  | LIGHT & SMALL POWER | 0.4
CR | CRUSHER | 0.8 | 0.6 |  |  |  |  | FANS | 0.8
CV | CONVEYOR | 0.9 | 0.95 |  |  |  |  | SAMPLERS | 0
DC | DUST COLLECTOR | 0.7 | 0.95 |  |  |  |  | HOISTS | 0.2
DR | DRIER | 0.8 | 0.95 |  |  |  |  | STANDBY DRIVES | 0
FC | FLOTATION CELL | 0.8 | 0.95
FD | FEEDER | 0.85 | 0.95
FN | FAN / BLOWER | 0.8 | 0.95
FT | FILTER | 0.8 | 0.95
GA | GATE (ISOLATION) | 0.8 | 0.1
HE | HEATER / OVEN | 1 | 0.95
HP | HYDRAULIC POWER PACK | 0.7 | 0.95
HPP | HYDRAULIC POWER PACK | 0.7 | 0.95
HX | HEAT EXCHANGER | 0.9 | 0.95
LS | LUBRICATION SYSTEM | 0.7 | 0.95
MD | METAL DETECTOR | 0.8 | 0.95
MG | MAGNET | 1 | 0.95
ML | MILL | 0.75 | 0.95
MS | MAGNETIC SEPARATOR | 0.7 | 0.95
PP | PUMP | 0.75 | 0.95
RB | ROCK BREAKER | 0.75 | 0.1
SA | SAMPLER | 0.9 | 0.1
SK | STACK / FLUE
SN | SCREEN | 0.9 | 0.95
ST | SHAKING TABLE | 0.8 | 0.95
TH | THICKENER | 0.7 | 0.95
WN | WINCH | 0.9 | 0.1
WT | WEIGHTOMETER / SCALE | 0.7 | 0.95
XA |  | 0.75 | 0.95
XM |  | 1 | 0.95
| NOTES :- | LOAD FACTOR IS A CONSIDERATION THAT THE MOTOR SELECTED FOR THE PARTICULAR
DUTY IS OVERSIZED TO ACCOMODATE THE CALCULATED DEMAND FROM THE MACHINE AND
AN ASSUMPTION THAT ANY DRIVE WILL NOT NORMALLY HAVE 100% LOAD AT ALL TIMES.
(DIVERSITY FACTOR)